Date:	11/18/2013
Vendor Name:		BACnet Stack hosted on SourceForge.net
Product Name:		Server Simulation
Product Model Number:			GNU
Applications Software Version:				1	Firmware Revision:	0.9.0
BACnet Protocol Revision:				14

Product Description:
Example BACnet server device used with the BACnet Stack hosted on SourceForge.net

BACnet Standardized Device Profile (Annex L)
	BACnet Operator Workstation (B-OWS)
	BACnet Building Controller (B-BC)
	BACnet Advanced Application Controller (B-AAC)
x	BACnet Application Specific Controller (B-ASC)
	BACnet Smart Sensor (B-SS)
	BACnet Smart Actuator (B-SA)

List all BACnet Interoperability Building Blocks supported (see Annex K in BACnet Addendum 135d):
DS-RP-B Read Property / DS-WP-B Write Property / DM-DDB-B Dynamic Device Binding / DM-DOB-B Dynamic Object Binding / DM-DCC-B Device Communication Control / DS-RPM-B ReadPropertyMultiple / DS-WPM-B WritePropertyMultiple / DM-RD-B Reinitialize Device / DS-COVU-A,B UnconfirmedCOV

Which of the following device binding methods does the product support? (check one or more)
	Send Who-Is, receive I-Am (BIBB DM-DDB-A)
x	Receive Who-Is, send I-Am (BIBB DM-DDB-B)
	Send Who-Has, receive I-Have (BIBB DM-DOB-A)
x	Receive Who-Has, send I-Have (BIBB DM-DOB-B)
	Manual configuration of recipient device's network number and MAC address
	None of the above

Standard Object Types Supported:

Analog Input Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description
	4. List of all properties that are writable where not otherwise required by this standard

	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning
9997		REAL	Test case for REAL
9998		Unsigned	Test case for positive value encoding
9999		Signed	Test case for negative value encoding
	6. List of any property value range restrictions:
Property Identifier		Restrictions

List of non-dynamic object identifiers and their meaning in this device
Object Identifier		Meaning
Analog Input 0		demo object - no meaning
Analog Input 1		demo object - no meaning
Analog Input 2		demo object - no meaning
Analog Input 3		demo object - no meaning

Analog Output Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description
	4. List of all properties that are writable where not otherwise required by this standard
Out_Of_Service
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions
Present_Value		0-100%, 1% resolution

List of non-dynamic object identifiers and their meaning in this device
Object Identifier		Meaning
Analog Output 0		demo object - no meaning
Analog Output 1		demo object - no meaning
Analog Output 2		demo object - no meaning
Analog Output 3		demo object - no meaning

Analog Value Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description, Priority_Array, Relinquish_Default
	4. List of all properties that are writable where not otherwise required by this standard
Present_Value / Out_Of_Service
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions
Present_Value		0-100%, 1% resolution.

Binary Input Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description
	4. List of all properties that are writable where not otherwise required by this standard
Present_Value / Out_Of_Service
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions

Binary Output Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description, Active_Text, Inactive_Text
	4. List of all properties that are writable where not otherwise required by this standard
Out_Of_Service
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions

Binary Value Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description, Active_Text, Inactive_Text
	4. List of all properties that are writable where not otherwise required by this standard
Present_Value / Out_Of_Service
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions

File Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description
	4. List of all properties that are writable where not otherwise required by this standard
File_Size
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions

Life Safety Point Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description
	4. List of all properties that are writable where not otherwise required by this standard
Out_Of_Service
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions

Load Control Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description, Full_Duty_Baseline
	4. List of all properties that are writable where not otherwise required by this standard

	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions

Multi-state Input Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description
	4. List of all properties that are writable where not otherwise required by this standard
Out_Of_Service
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions
Present_Value		0-254 states

Multi-state Output Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description
	4. List of all properties that are writable where not otherwise required by this standard
Out_Of_Service
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions
Present_Value		0-254 states

Multi-state Value Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description
	4. List of all properties that are writable where not otherwise required by this standard
Out_Of_Service
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions
Present_Value		0-254 states

Characterstring Value Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description
	4. List of all properties that are writable where not otherwise required by this standard
Out_Of_Service
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions
Present_Value		0-254 states

Channel Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:

	4. List of all properties that are writable where not otherwise required by this standard
Out_Of_Service
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions
Present_Value		0-254 states

Lighting Output Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description
	4. List of all properties that are writable where not otherwise required by this standard
Out_Of_Service
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions
Present_Value		0-254 states

Device Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:

	4. List of all properties that are writable where not otherwise required by this standard
Object_Name
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions
Object_Name		< 16 characters
Object_Identifier		Device Type only.
Number_Of_APDU_Retries		0-255
APDU_Timeout		0-65535 milliseconds
Vendor_Identifier		0-65535
System_Status

Data Link Layer Options (check all that are supported):

X	BACnet IP, (Annex J)
	BACnet IP, (Annex J), Foreign Device
	ISO 8802-3, Ethernet (Clause 7)
	ANSI/ATA 878.1, 2.5 Mb. ARCNET (Clause 8)
	ANSI/ATA 878.1, RS-485 ARCNET (Clause 8), baud rate(s):
	MS/TP master (Clause 9), baud rate(s):
	MS/TP slave (Clause 9), baud rate(s):
	Point-To-Point, EIA 232 (Clause 10), baud rate(s):
	Point-To-Point, modem, (Clause 10), baud rate(s):
	LonTalk, (Clause 11), medium:
	Other:

Networking Options (check all that are supported):

	Router, Clause 6 - List all routing configurations (e.g. ARCNET-Ethernet, Ethernet-MS/TP, etc.):

	Annex H.3, BACnet Tunneling Router over UDP/IP
X	BACnet/IP Broadcast Management Device (BBMD)
X	BBMD supports registrations by Foreign Devices

Segmentation Capability (check all that apply):
	Window Size
Segmented requests supported
Segmented responses supported

Character Sets Supported (check all that apply):
Indicating support for multiple character sets does not imply that they can all be supported simultaneously.

x	ANSI X3.4
	IBM/Microsoft DBCS
	ISO 8859-1
	ISO 10646 (UCS-2)
	ISO 10646 (ICS-4)
	JIS C 6226

If this product is a communication gateway, describe the non-BACnet equipment/network(s) that the gateway supports:
N/A

Include any addition information about the product's BACnet capabilities relevant to interoperability: